## VIPA GmbH 09.11.2000

## Profibus Slave VIPA 253-1DP00, VIPA 253-1DP10, VIPA 253-1DP02, VIPA 253-1DP12

## Systemeigenschaften

- Power supply of connected System 200V modules with up to 3A

- Power down recognition at 8.5V

- Maximum of 152 byte Input and 152 byte Output data

- Maximum of 152 byte parameter data

- Maximum of 32 byte diagnostic data

- Supports all Profibus data rates

- Possible Profibus addresses are 1..126  (A startup with address 0 is not valid because it is reserved for a Profibus master. In that case the LED indicators RDY and ERR are flashing together.) After a startup with a valid Profibus address, slaves with address switches can execute two special functions:

- After a startup with System 200V modules connected, changing to address 00 causes a single flash store operation of the internal diagnostics buffer.

- After a startup without modules connected, the EEPROM and the internal diagnostic data in flash is cleared. When finished, the RDY LED lights up and the slave is halted.

- Min_Slave_Intervall:  This parameter of the GSD file is by default set to 3ms. Depending on the amount of System 200V modules, the value be changed  between 0.2ms and 4ms (The Profibus Slave guarantees to the Profibus Master, that after a time of Min_Slave_Intervall  all input data is read and all output data is written!)

## LED Indicators

| # Bezeichnung |  | Farbe | Bedeutung |
| --- | --- | --- | --- |
| PW | Power | Yellow | Lights up, when power supply is alright. |
| ER | Error | Red | Lights up for a short time at startup (=power up). Is switched on when a internal error occured. Flashes if an initialization error happened (e.g. unknown module detected) Flashes alternately with RD when received wrong configuration data. Flashes together with RD when a parameterization error happened. (e.g. you sent parameter data to a nonconfigurable modules like a digital module) |
| RD | Ready | Green | Flashes after self test and initialization procedure are passed with OK. Is switched on in state Data Exchange if the vbus-cycle time is faster than the profibus cycle time (Thats the way your system should run!). Is switched off in state Data Exchange if the vbus-cycle time is slower than the Profibus-cycle time (In this case not all telegrams can be sent to the modules and you loose data!) |
| DE | Data Exchange | Yellow | Is switched on in state Data Exchange, which means that a connection with the Profibus master has been established and IO Data is exchanged. |

## Aufbau der Diagnose IM253DP/DPV1

| # Byte |  |  |
| --- | --- | --- |
| 0 | Profibus Norm Diagnostics, see VIPA manual |  |
| 1 |  |  |
| 2 |  |  |
| 3 |  |  |
| 4 |  |  |
| 5 |  |  |
| 6 | Header for vendor specific Diagnostics |  |
| 7 | Message type | Hex, Dez, Message 0A = 10: DP-parameterization error 14 = 20: DP-configuration length error 15 = 21: DP-configuration entry error 1E = 30: power fail / power off 28 = 40: VBUS-parameterization error 29 = 41: VBUS-initialization error 2A = 42: VBUS-bus error 2B = 43: VBUS-read/write error (=Quittungsverzug) 32,34 = 50,52: diagnostics alert of a System 200 module 33,35 = 51,53: process alert of a System 200 module 3C = 60: New DP address was set 3D = 61: Slave entered state READY 3E = 62: Slave entered state DATA_EXCHANGE |
| 8 | Slot (=module number) | 1 to 32 |
| 9-29 | Additional information to 7 | (see following tables) |

DP-parameterization error (Message type: 0Ahex  = 10dez )

This diagnostic message is created of the parameter telegram is too short  or too long.

| # Byte |  |  |
| --- | --- | --- |
| 0..5 | Profibus Norm Diagnostics see VIPA manual |  |
| 6 | Length of diagnostic data | 7 |
| 7 | Message type | 10 |
| 8 | Modulnummer, Steckplatz (1..32) | 0 |
| 9 | Length of user parameter data |  |
| 10 | S7-Mode | 0 : Standard mode 1 : S7-400 Special Mode |
| 11 | Number of Digital modules (Slave) |  |
| 12 | Number of Analog modules (Slave) |  |
| 13 | Number of Analog modules (Master) |  |

DP-configuration length error  (Message type: 14hex = 20dez)

The length of the configuration telegram is compared with the recognized modules on the vbus.

| # Byte |  |  |
| --- | --- | --- |
| 0..5 | Profibus Norm Diagnostics see VIPA manual |  |
| 6 | Length of diagnostic data | 6 |
| 7 | Message type | 20 |
| 8 | Slot number (1..32) | 0 |
| 9 | Number of configuration bytes (Master) |  |
| 10 | Number of configuration bytes (Slave) |  |
| 11 | S7-Mode | 0 : Standard mode 1 : S7-400 Special Mode |

DP-configuration entry error (Message type: 15hex = 21dez )

The configuration bytes, sent from from master, are compared with the configuration bytes which are created by the slaves depending on the attached System 200V modules.

| # Byte |  |  |
| --- | --- | --- |
| 0..5 | Profibus Norm Diagnostics see VIPA manual |  |
| 6 | Length of diagnostic data | 6 |
| 7 | Message type | 21 |
| 8 | Slot number (1..32) |  |
| 9 | Configuration byte (Master) |  |
| 10 | Configuration byte (Slave) |  |
| 11 | S7-Mode | 0 : Standard mode 1 : S7-400 Special Mode |

VBUS-Parameterization error (Message type: 28hex = 40dez)

Sending Parameters to slot number x was not successfull.

| # Byte |  |  |
| --- | --- | --- |
| 0..5 | Profibus Norm Diagnostics see VIPA manual |  |
| 6 | Length of diagnostic data | 3 |
| 7 | Message type | 40 |
| 8 | Slot number (1..32) |  |

VBUS-Initialization error (Message type: 29hex = 41dez )

Internal Error at initialization or a unknown module was recognized on VBUS.

| # Byte |  |  |
| --- | --- | --- |
| 0..5 | Profibus Norm Diagnostics see VIPA manual |  |
| 6 | Length of diagnostic data | 2 |
| 7 | Message type | 41 |

VBUS-Bus error (Message type: 2Ahex = 42dez)

Hardware error or module dropout.

| # Byte |  |  |
| --- | --- | --- |
| 0..5 | Profibus Norm Diagnostics see VIPA manual |  |
| 6 | Length of diagnostic data | 2 |
| 7 | Message type | 42 |

VBUS-Read/Write error (=Quittungsverzug) (Message type 2Bhex = 43dez)

An error happened in a read or write-operation.

| # Byte |  |  |
| --- | --- | --- |
| 0..5 | Profibus Norm Diagnostics see VIPA manual |  |
| 6 | Length of diagnostic data | 3 |
| 7 | Message type | 43 |
| 8 | Slot number (1..32) (255 = unknown) |  |

Diagnostics alert of a System 200V module (Message type 32hex = 50dez, Message type 34hex = 52dez)

| # Byte |  |  |
| --- | --- | --- |
| 0..5 | Profibus Norm Diagnostics see VIPA manual |  |
| 6 | Length of diagnostic data | 19 |
| 7 | Message type | 50,52 |
| 8 | Slot number (1..32) |  |
| 9..21 | Diagnostic data of the System 200V module (see manual) |  |

Process alert of a System 200V module (Message type 33hex = 51dez, Message type 35hex = 53dez)

| # Byte |  |  |
| --- | --- | --- |
| 0..5 | Profibus Norm Diagnostics see VIPA manual |  |
| 6 | Length of diagnostic data | 19 |
| 7 | Message type | 51,53 |
| 8 | Slot number (1..32) |  |
| 9..21 | Process alert data of the System 200V module (see manual) |  |

New DP address was set (Message type: 3Chex = 60dez )

After acceptance of the service ‘Set Slave Address’ the slave sends the following diagnosis message and reboots. Then the slave is active on network with his new address!.

| # Byte |  |  |
| --- | --- | --- |
| 0..5 | Profibus Norm Diagnostics see VIPA manual |  |
| 6 | Length of diagnostic data | 2 |
| 7 | Message type | 60 |

Changes against the old IM253DP-Slave

- Maximum of 32 Modules

- Maximum of  16 Analog modules

- The slot number, which can be selected in a Profibus configuration tool is not evaluated in the firmware anymore.

- New Diagnostic messages as described above.

- Storage of the last 100 diagnostic messages with a timestamp inside flash. Reading out this information is possible with the tool “slave info” and the vipa download wire.

- Slaves with a Display have got additional diagnostic, measurement and test functionality: Number of modules, display of last diagnostic message, measurement of vbus-cycle time and profibus cycle time, test set outputs und test read inputs without profibus connection...

GSD-file:

- The Profibus Slave is delivered with a new GSD-file version 1.13.

- The Slave also runs in Systems, which were configured with former GSD file versions.

- Exception: If you use nonconfigurable analog modules (231-1BD10, 231-1BD60, 231-1BD70, 232-1BD70) together with configurable analog modules you need to reconfigure the whole Profibus system with the new GSD file version 1.13 because else the parameter data will not be sent to the correct slot!

- New GSD-file: Max_Module 32, 2 dummy-Parameter bytes for nonconfigurable analog modules inserted, new global slave parameter “Sync Mode”.

- The Min_Slave_Intervall 30 (=3ms) was retained as default value. With the measurement feature of the Vbus-cycle time (only Slaves with Display) it is possible to optimize that value depending on the modular enlargement of your Slave system.